## Slide 1: MODBUS

## Slide 2: MODBUS
MODBUS Protocol is a messaging structure developed by Modicon in 1979
Master-slave/client-server communication between intelligent devices
De facto standard
Open
Most widely used network protocol in the industrial manufacturing environment

## Slide 3: MODBUS
Application protocol OSI 7
  client/server
  Port TCP/IP 502
  request/reply protocol offering services specified by function codes
Over serial line protocol OSI 2
  master(client)/slave(server)
  request/reply protocol

## Slide 4: MODBUS application protocol
Simple PDU independant of the underlying communication layer (max size = 253 bytes)
  PDU = [FuntionCode][Data]
ADU = PDU + additionnal fields related to specific buses or networks
  ADU = [Additional adress][FuntionCode][Data][ErrorCheck]
    RS232/RS485 ADU max size = 256 bytes
    TCP/IP ADU max size = 260 bytes
Big-Endian representation (to send 0x1234 the first byte sent is 0x12 then 0x34)

## Slide 5: MODBUS over serial line protocol
Modbus PDU (max 253 bytes) = [FuntionCode][Data]
Modbus serial line PDU = (max 256 bytes) = [Additional field][FuntionCode][Data][CRC (or LRC)]
2 transmission modes
  RTU [SlaveAdress 1 byte][FunctionCode 1 byte][Data max 252 bytes][CRC 2 bytes]
  ASCII [Start 1 char :][Adress 2 chars][Function 2 chars][Data max 2*252 chars][LRC 2 chars][End 2 chars CR,LF]

## Slide 6: MODBUS PDU and Function Codes
3 types of PDUs
  Request
  Response
  Error
3 classes of function codes
  Public
    Unique and guaranted by MDOBUS-IDA.org
  User-defined
    No guaranted on uniqueness
  Reserved
    Private, used by some companies on legacy products

## Slide 7: MODBUS data model
Based of 4 primary tables
Primary tables | Object type | Type of | Comments
Discrete Input | Single bit | Read-Only | can be provided by an I/O system
Coils | Single bit | Read-Write | can be altered by an apllication program
Input Registers | 16-bit word | Read-Only | can be provided by an I/O system
Holding Registers | 16-bit word | Read-Write | can be altered by an apllication program

## Slide 8: MODBUS data model
Distinction between tables is conceptual => the tables may be overlaying one another.
For each primary table the protocol allow individual selection of 65536 data items.
All data handled via MODBUS (bits or registers) must be allocated in device application memory but physical adress in memory should not be confused with data reference.
MODBUS logical reference are unsigned integer starting at 0.

## Slide 9: MODBUS over serial : openAT implementation
Asynchronous (callback driven) modbus stack.
MODBUS_InitContext to initialize the stack
  Set the line parameters (mainly, parity, baudrate, timeout) and the modbus mode (RTU or ASCII).
  Register a callback to receive MODBUS responses
MODBUS_ReleaseContext to close the stack
Enable/disable a GPIO pin to signal Rx/Tx phases
  MODBUS_EnableHardwareSwitch
  MODBUS_DisableHardwareSwitch

## Slide 10: MODBUS over serial : openAT implementation
8 main MODBUS functions
  MODBUS_ReadCoils
  MODBUS_ReadDiscreteInputs
  MODBUS_ReadHoldingRegisters
  MODBUS_ReadInputRegisters
  MODBUS_WriteSingleCoil
  MODBUS_WriteSingleRegister
  MODBUS_WriteMultipleCoils
  MODBUS_WriteMultipleRegisters

## Slide 11: MODBUS over serial : Lua implementation
Synchronous thread safe.
Requires ‘modbus’ and ‘pack’.
m,err=modbus.new() to initialize the stack with default parameters.
  m,err=modbus.new('uart2',{baudrate=9600,parity='even',
  timeout=3}, 'rtu')
m:close() to close the stack.
Start or stop a GPIO pin to signal Rx/Tx phases
  _,err = m:enable_hardware_switch(12,'high')
  _,err = m:disable_hardware_switch()

## Slide 12: MODBUS over serial : Lua implementation
8 main MODBUS functions
  <values>,err=m:request('ReadCoils',<slaveid>,<startingaddr>,<number>)
  <values>,err=m:request('ReadDiscreteInputs',<slaveid>,<startingaddr>,<number>)
  <values>,err=m:request('ReadHoldingRegisters',<slaveid>,<startingaddr>,<number>)
  <values>,err=m:request('ReadInputRegisters',<slaveid>,<startingaddr>,<number>)
  _,err=m:request('WriteSingleCoil',<slaveid>,<startingaddr>,<state>)
  _,err=m:request('WriteSingleRegister',<slaveid>,<startingaddr>,<value>)
  _,err=m:request('WriteMultipleCoils',<slaveid>,<startingaddr>,<number>,<values>)
  _,err=m:request('WriteMultipleRegisters',<slaveid>,<startingaddr>,<values>)